Voltage table for cyclic use charging. The higher voltages (above the gassing voltage) should only be used on flooded batteries that can have the water replaced:

| Battery Temperature | Charge Voltage per cell | Charge Voltage for a 12 Volt battery | Gassing Voltage per cell | Gassing Voltage for a 12V battery |
| --- | --- | --- | --- | --- |
| -20 °C * | 2.67 to 2.76 | 16.02 to 16.56 | 2.97 | 17.82 |
| -10 °C * | 2.61 to 2.70 | 15.66 to 16.2 | 2.65 | 15.9 |
| 0 ° C * | 2.55 to 2.65 | 15.3 to 15.9 | 2.54 | 15.24 |
| 10 °C | 2.49 to 2.59 | 14.94 to 15.54 | 2.47 | 14.82 |
| 20 °C | 2.43 to 2.53 | 14.58 to 15.18 | 2.415 | 14.49 |
| 25 °C | 2.40 to 2.50 | 14.40 to 15.00 | 2.39 | 14.34 |
| 30 °C | 2.37 to 2.47 | 14.22 to 14.82 | 2.365 | 14.19 |
| 40 °C | 2.31 to 2.41 | 13.86 to 14.46 | 2.33 | 13.98 |
| 50 °C | 2.25 to 2.35 | 13.5 to 14.10 | 2.30 | 13.8 |

Voltage table for standby use charging:

| Battery Temperature | Charge Voltage per cell | Charge Volage for 12V Battery | Gassing voltage |
| --- | --- | --- | --- |
| -30 °C * | 2.7 | 16.2 |  |
| -20 °C * | 2.34 to 2.38 | 14.04 to 14.28 | 2.97 |
| -10 °C * | 2.32 to 2.37 | 13.92 to 14.22 | 2.65 |
| 0 °C | 2.30 to 2.35 | 13.8 to 14.1 | 2.54 |
| 10 °C | 2.28 to 2.33 | 13.68 to 13.98 | 2.47 |
| 20 °C | 2.26 to 2.31 | 13.56 to 13.86 | 2.415 |
| 25 °C | 2.25 to 2.30 | 13.5 to 13.8 | 2.39 |
| 30 °C | 2.24 to 2.29 | 13.44 to 13.74 | 2.365 |
| 40 °C | 2.22 to 2.27 | 13.32 to 13.62 | 2.33 |
| 50 °C | 2.20 to 2.25 | 13.2 to 13.5 | 2.30 |

* Note that a fully discharged battery freezes solid at about 0°C, a fully
charged battery freezes about -40°C